## Panel Board 1
DISTRIBUTION BOARD - 1P
Voltage : 120V/208V |  |  |  | Bus Rating : 110A, 3PN
Phase : 3 |  |  |  | Main Breaker Rating : 125A, 3PN
Wire : 4 |  |  |  | Location Name : Electrical Room 202
Total Circuits : 34
Remarks | CCT No | Load |  |  |  | Breaker Size | Pole | Phase |  | Connected Load (VA) | Spare (VA)
|  | Description | Qty | Type | KVA |  |  |  | Phase R | 14423.5942 | 1920
| 1 | Receptacle - 41,35,38,82,84,1,5,56 | 8 | REC | 1437.7 | 20A | 1P | R | Phase Y | 13556.9083 | 1440
|  | Lighting - 45,38,39 | 3 | LTG |  |  |  |  | Phase B | 12043.1752 | 2400
|  | Other | 0 | OTH
| 2 | Receptacle - 87 | 1 | REC | 1410.9278 | 15A | 1P | Y | Load Summary (VA) |  | Diversity | Demand Load
|  | Lighting | 0 | LTG |  |  |  |  | Receptacle | 17100 | As per CEC for first 10KVA Diversity Factor is 1.0 & for rest 0.5 | 14784.55
|  | Other - Baseboard Heater#2, Chimney | 2 | OTH |  |  |  |  | Lighting | 2469.1
| 3 | Receptacle | 0 | REC | 1578.9474 | 60A | 1P | B | Other | 20454.5777 | 0.5 | 10227.2888
|  | Lighting | 0 | LTG |  |  |  |  | Spare | 5760 | 0.5 | 2880
|  | Other - Force Flow Fan#2 | 1 | OTH
| 4 | Receptacle - 44,45,46,63,66,55,57,58 | 8 | REC | 1440 | 20A | 1P | R
|  | Lighting | 0 | LTG |  |  |  |  | Total Demand (KVA) |  | 27.8918
|  | Other | 0 | OTH |  |  |  |  | Total Demand (Amps) |  | 77.4223
Receptacle 92 is 360VA | 5 | Receptacle - 90,95,91,92,85,98 | 6 | REC | 1378 | 20A | 1P | Y | Spare Load (Included in Total Demand) |  | 14.39%
|  | Lighting - 86,90 | 2 | LTG
|  | Other - CCTV#22,23 | 2 | OTH |  |  |  |  | NOTES : A. For the sake of simplicity efficiency and power factor for motors are considered 95% and 0.95 respectively. B. A. For the sake of simplicity power factor for baseboard heater are considered 0.95 respectively. C. For Lighting Load we have considered 0.99 Power Factor. D. All receptacles other than than remarks are of 180VA.
| 6 | Receptacle - 20,26,29,25,14,16,11 | 7 | REC | 1260 | 20A | 1P | B
|  | Lighting | 0 | LTG
|  | Other | 0 | OTH
| 7 | Receptacle - 68 | 1 | REC | 1354 | 20A | 1P | R
|  | Lighting - 46,47,48,53,55,56,59 | 7 | LTG
|  | Other - CCTV#14, Projector#3, Dryer(W) | 3 | OTH
| 8 | Receptacle - 74,61 | 2 | REC | 958 | 15A | 1P | Y
|  | Lighting - 85,68,83 | 3 | LTG
|  | Other - Projector#4 | 1 | OTH
| 9 | Receptacle | 0 | REC | 720 | 15A | 1P | B
|  | Lighting | 0 | LTG
|  | Other - Force Flow Fan#1 | 1 | OTH
| 10 | Receptacle - 71,72,73,77,80 | 5 | REC | 1306 | 20A | 1P | R
|  | Lighting - 60,61,62,66,67,71,72,78,82 | 9 | LTG
|  | Other - Dryer(M), Washroom Signage | 1 | OTH
Receptacle 67 is 360VA | 11 | Receptacle - 93,96,94,88,67 | 5 | REC | 1092 | 20A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - CCTV#25,16 | 2 | OTH
| 12 | Receptacle - 18,31 | 2 | REC | 1390.9278 | 20A | 1P | B
|  | Lighting | 0 | LTG
|  | Other - Baseboard Heater#3 | 1 | OTH
| 13 | Receptacle - 78,81 | 2 | REC | 1401.9278 | 20A | 1P | R
|  | Lighting - 76 | 1 | LTG
|  | Other - Baseboard Heater#5 | 1 | OTH
| 14 | Receptacle - 86,83,79,75,76,70,89 | 7 | REC | 1780 | 20A | 1P | Y
|  | Lighting - 97,95,96,91,92,89,87,88,80,81,75,73,74,65,63 | 15 | LTG
|  | Other | 0 | OTH
| 15 | Receptacle | 0 | REC | 720 | 15A | 1P | B
|  | Lighting | 0 | LTG
|  | Other - Force Flow Fan#4 | 1 | OTH
| 16 | Receptacle | 0 | REC | 1894.7368 | 70A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Dish Washer | 1 | OTH
| 17 | Receptacle | 0 | REC | 842.1053 | 15A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - Fridge | 1 | OTH
| 18 | Receptacle - 2,3,4,6,7,8 | 6 | REC | 1119.1 | 20A | 1P | B
|  | Lighting - 1 | 1 | LTG
|  | Other | 0 | OTH
| 19 | Receptacle | 0 | REC | 1855.6701 | 20A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Electrical Oven/Range | 1 | OTH
Receptacle 52 & 62 is 90VA | 20 | Receptacle - 64,65,60,52,62,51,40,49 | 8 | REC | 1336 | 20A | 1P | Y
|  | Lighting - 58,51,57,50,44 | 5 | LTG
|  | Other | 0 | OTH
Receptacle 17 is 90VA | 21 | Receptacle - 9,10,12,13,15,23,19,17 | 8 | REC | 1350 | 20A | 1P | B
|  | Lighting | 0 | LTG
|  | Other | 0 | OTH
| 22 | Receptacle | 0 | REC | 1052.6316 | 20A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Fridge | 1 | OTH
Receptacle 50 is 360VA | 23 | Receptacle - 42,48,43,53,59,50,97 | 6 | REC | 1370 | 20A | 1P | Y
|  | Lighting - 49,52,42 | 3 | LTG
|  | Other - CCTV#15 | 1 | OTH
| 24 | Receptacle - 22,24,27,28 | 4 | REC | 1378 | 20A | 1P | B
|  | Lighting - 7,8,9,11,12,13 | 6 | LTG
|  | Other - Projector#1, CCTV#2 | 2 | OTH
| SPARE |  |  |  |  | 20A | 1P | R
| 25 | Receptacle - 69 | 1 | REC | 1210.9278 | 15A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - Baseboard Heater#8 | 1 | OTH
| 26 | Receptacle - 32,33 | 2 | REC | 1211.2 | 15A | 1P | B
|  | Lighting - 15,16,17,20,21,22,23,24,26,28,30,27,29,31,32,33,34,35 | 18 | LTG
|  | Other - CCTV#4,6,8 Projector#2 | 2 | OTH
| 27 | Receptacle - 36,47 | 2 | REC | 1390.9278 | 20A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Baseboard Heater#9 | 1 | OTH
| 28 | Receptacle | 0 | REC | 600 | 15A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - Hot Water Tank | 1 | OTH
Receptacle 39 is 360VA | 29 | Receptacle - 34,39,30,37,21 | 5 | REC | 1315 | 20A | 1P | B
|  | Lighting - 36,37,18,19 | 4 | LTG
|  | Other - CCTV#7,9 | 2 | OTH
| 30 | Receptacle | 0 | REC | 1578.9474 | 60A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - Force Flow Fan#3 | 1 | OTH
| 31 | Receptacle | 0 | REC | 1290 | 15A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Projector#5,6,7 | 1 | OTH
| SPARE |  |  |  |  | 25A | 1P | Y
| SPARE |  |  |  |  | 15A | 1P | B

## Panel Board 2
DISTRIBUTION BOARD - 2P
Voltage : 208V |  |  |  | Bus Rating : 20A, 3PN
Phase : 3 |  |  |  | Main Breaker Rating : 20A, 3PN | [5 empty] | Connected Load (VA) | Spare (VA)
Wire : 4 |  |  |  | Location Name : Electrical Room 202 |  |  |  |  | Phase R-Y-B | 10320 | 960
Total Circuits : 5
Remarks | CCT No | Load |  |  |  | Breaker Size | Pole | Phase
|  | Description | Qty | Type | KVA
| 1 | Receptacle | 0 | REC | 2.5773 | 10A | 2P | R-Y | Load Summary (VA) |  | Diversity | Demand Load
|  | Lighting | 0 | LTG |  |  |  |  | Receptacle | 0 | As per CEC for first 10KVA Diversity Factor is 1.0 & for rest 0.5 | 0
|  | Baseboard Heater#1 | 1 | HTR |  |  |  |  | Lighting | 0
| 2 | Receptacle | 0 | REC | 2.5773 | 10A | 2P | Y-B | Baseboard Heater | 10320 | 0.5 | 5160
|  | Lighting | 0 | LTG |  |  |  |  | Spare | 960 | 0.5 | 480
|  | Baseboard Heater#4 | 1 | HTR
| 3 | Receptacle | 0 | REC | 2.5773 | 10A | 2P | R-B
|  | Lighting | 0 | LTG |  |  |  |  | Total Demand (KVA) |  | 5.64
|  | Baseboard Heater#6 | 1 | HTR |  |  |  |  | Total Demand (Amps) |  | 15.6736
| 4 | Receptacle | 0 | REC | 2.5773 | 10A | 2P | R-Y | Spare Load (Included in Total Demand) |  | 9.302%
|  | Lighting | 0 | LTG
|  | Baseboard Heater#7 | 1 | HTR |  |  |  |  | NOTES : A. For the sake of simplicity power factor for baseboard heater are considered 0.95 respectively.
| 5 | SPARE |  |  |  | 10A | 1P | B

## Panel Board 3
DISTRIBUTION BOARD - 3P
Voltage : 208V |  |  |  | Bus Rating : 110A, 3PN
Phase : 3 |  |  |  | Main Breaker Rating : 110A, 3PN | [5 empty] | Connected Load (VA) | Spare (VA)
Wire : 4 |  |  |  | Location Name : Electrical Room 202 |  |  |  |  | Phase R-Y-B | 55215.8892 | 5760
Total Circuits : 10
Remarks | CCT No | Load |  |  |  | Breaker Size | Pole | Phase
|  | Description | Qty | Type | KVA
| 1 | Receptacle | 0 | REC | 5.0378 | 35A | 3P | R-Y-B | Load Summary (VA) |  | Diversity | Demand Load
|  | Lighting | 0 | LTG |  |  |  |  | Receptacle | 0 | As per CEC for first 10KVA Diversity Factor is 1.0 & for rest 0.5 | 0
|  | Condensate Unit#1 | 1 | CU |  |  |  |  | Lighting | 0
| 2 | Receptacle | 0 | REC | 6.4771 | 45A | 3P | R-Y-B | Condensate | 38862.72 | 0.5 | 19431.36
|  | Lighting | 0 | LTG |  |  |  |  | Exhaust Fan | 1239.8892 | 1 | 1239.8892
|  | Condensate Unit#2 | 1 | CU |  |  |  |  | Furnace | 15113.28 | 0.5 | 7556.64
| 3 | Receptacle | 0 | REC | 14.0338 | 90A | 3P | R-Y-B | Spare | 5760 | 0.5 | 2880
|  | Lighting | 0 | LTG
|  | Condensate Unit#3 | 1 | CU
| 4 | Receptacle | 0 | REC | 13.3141 | 90A | 3P | R-Y-B | Total Demand (KVA) |  | 31.1079
|  | Lighting | 0 | LTG |  |  |  |  | Total Demand (Amps) |  | 86.4492
|  | Condensate Unit#4 | 1 | CU |  |  |  |  | Spare Load (Included in Total Demand) |  | 10.43%
| 5 | Receptacle | 0 | REC | 1.2399 | 15A | 3P | R-Y-B
|  | Lighting | 0 | LTG |  |  |  |  | NOTES : A. For the sake of simplicity Diversity Factor for all the equipments is as shown in the above table. B. For the sake of simplicity efficiency and power factor for motors are considered 95% and 0.95 respectively.
|  | Exhaust Fan#2 | 1 | EF
| 6 | Receptacle | 0 | REC | 3.5984 | 20A | 3P | R-Y-B
|  | Lighting | 0 | LTG
|  | Furnace#1 | 1 | FUR
| 7 | Receptacle | 0 | REC | 3.5984 | 15A | 3P | R-Y-B
|  | Lighting | 0 | LTG
|  | Furnace#2 | 1 | FUR
| 8 | Receptacle | 0 | REC | 3.5984 | 15A | 3P | R-Y-B
|  | Lighting | 0 | LTG
|  | Furnace#3 | 1 | FUR
| 9 | Receptacle | 0 | REC | 4.3181 | 15A | 3P | R-Y-B
|  | Lighting | 0 | LTG
|  | Furnace#4 | 1 | FUR
| 10 | SPARE |  |  |  | 20A | 3P | R-Y-B

## Panel Board U
DISTRIBUTION BOARD - U
Voltage : 120/208V |  |  |  | Bus Rating : 110A, 3PN
Phase : 3 |  |  |  | Main Breaker Rating : 110A, 3PN | [5 empty] | Connected Load (VA) | Spare (VA)
Wire : 4 |  |  |  | Location Name : Electrical Room 202 |  |  |  |  | Phase R-Y-B | 17870.5042 | 4320
Total Circuits : 7
Remarks | CCT No | Load |  |  |  | Breaker Size | Pole | Phase
|  | Description | Qty | Type | KVA
| 1 | Receptacle | 0 | REC | 16.5319 | 110A | 3P | R-Y-B | Load Summary (VA) |  | Diversity | Demand Load
|  | Lighting | 0 | LTG |  |  |  |  | Receptacle | 0 | As per CEC for first 10KVA Diversity Factor is 1.0 & for rest 0.5 | 1072.0082
|  | Fire Pump | 1 | FP |  |  |  |  | Lighting | 1072.0082
| 2 | Receptacle | 0 | REC | 0.382 | 15A | 1P | R | Fire Pump | 16531.856 | 1 | 16531.856
|  | Lighting - 40,84,69,54,43,14,70,77 | 8 | LTG |  |  |  |  | Other | 266.64 | 1 | 266.64
|  | Other - CCTV#11,13,20 | 3 | CU |  |  |  |  | Spare | 4320 | 0.75 | 3240
| 3 | Receptacle | 0 | REC | 0.359 | 15A | 1P | Y
|  | Lighting - 94,64,79,93,41,25,10,4,5 | 9 | LTG
|  | Other - CCTV#18,21,12,5,3,19 | 6 | CU |  |  |  |  | Total Demand (KVA) |  | 21.1105
| 4 | Receptacle | 0 | REC | 0.59765 | 15A | 1P | B | Total Demand (Amps) |  | 58.5986
|  | Lighting - 2,3,6,98,99 | 3 | LTG |  |  |  |  | Spare Load (Included in Total Demand) |  | 24.17%
|  | Other - Exhaust Fan#1, CCTV#26, Exit Signages, Fire sensors | 2 | CU
| 5 | SPARE |  |  |  | 15A | 1P | R | NOTES : A. For the sake of simplicity Diversity Factor for all the equipments is as shown in the above table.
| 6 | SPARE |  |  |  | 15A | 1P | Y
| 7 | SPARE |  |  |  | 15A | 1P | B