## Panel Board 1
DISTRIBUTION BOARD - 1P
Voltage : 120V/208V |  |  |  | Bus Rating : 110A, 3PN
Phase : 3 |  |  |  | Main Breaker Rating : 125A, 3PN
Wire : 4 |  |  |  | Location Name : Electrical Room 202
Total Circuits : 34
Remarks | CCT No | Load |  |  |  | Breaker Size | Pole | Phase |  | Connected Load (VA) | Spare (VA)
|  | Description | Qty | Type | KVA |  |  |  | Phase R | 14218.7 | 1920
| 1 | Receptacle - 41,35,38,82,84,1,5,56 | 8 | REC | 1437.7 | 20A | 1P | R | Phase Y | 13303 | 1440
|  | Lighting - 45,38,39 | 3 | LTG |  |  |  |  | Phase B | 12080.3 | 2400
|  | Other | 0 | OTH
| 2 | Receptacle - 87 | 1 | REC | 1410 | 15A | 1P | Y | Load Summary (VA) |  | Diversity | Demand Load
|  | Lighting | 0 | LTG |  |  |  |  | Receptacle | 17100 | As per CEC for first 10KVA Diversity Factor is 1.0 & for rest 0.5 | 14784.55
|  | Other - Baseboard Heater#2, Chimney | 2 | OTH |  |  |  |  | Lighting | 2469.1
| 3 | Receptacle | 0 | REC | 1579 | 30A | 1P | B | Other | 20032.9 | 0.5 | 10016.45
|  | Lighting | 0 | LTG |  |  |  |  | Spare | 5760 | 0.5 | 2880
|  | Other - Force Flow Fan#2 | 1 | OTH
| 4 | Receptacle - 44,45,46,63,66,55,57,58 | 8 | REC | 1440 | 20A | 1P | R
|  | Lighting | 0 | LTG |  |  |  |  | Total Demand (KVA) |  | 27.681
|  | Other | 0 | OTH |  |  |  |  | Total Demand (Amps) |  | 76.837
Receptacle 92 is 360VA | 5 | Receptacle - 90,95,91,92,85 | 5 | REC | 1198 | 20A | 1P | Y | Spare Load (Included in Total Demand) |  | 14.54%
|  | Lighting - 86,90 | 2 | LTG
|  | Other - CCTV#22,23 | 2 | OTH |  |  |  |  | NOTES : A. For the sake of simplicity efficiency and power factor for motors are considered 95% and 0.95 respectively. B. For Lighting Load we have considered 0.99 Power Factor. C. All receptacles other than than remarks are of 180VA.
| 6 | Receptacle - 20,26,29,25,14,16,11 | 7 | REC | 1260 | 20A | 1P | B
|  | Lighting | 0 | LTG
|  | Other | 0 | OTH
| 7 | Receptacle - 68 | 1 | REC | 1354 | 20A | 1P | R
|  | Lighting - 46,47,48,53,55,56,59 | 7 | LTG
|  | Other - CCTV#14, Projector#3, Dryer(W) | 3 | OTH
| 8 | Receptacle - 74,61 | 2 | REC | 958 | 15A | 1P | Y
|  | Lighting - 85,68,83 | 3 | LTG
|  | Other - Projector#4 | 1 | OTH
| 9 | Receptacle | 0 | REC | 720 | 15A | 1P | B
|  | Lighting | 0 | LTG
|  | Other - Force Flow Fan#1 | 1 | OTH
| 10 | Receptacle - 71,72,73,77,80 | 5 | REC | 1306 | 20A | 1P | R
|  | Lighting - 60,61,62,66,67,71,72,78,82 | 9 | LTG
|  | Other - Dryer(M), Washroom Signage | 1 | OTH
Receptacle 67 is 360VA | 11 | Receptacle - 93,96,94,88,67 | 5 | REC | 1092 | 20A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - CCTV#25,16 | 2 | OTH
| 12 | Receptacle - 18,31 | 2 | REC | 1390 | 20A | 1P | B
|  | Lighting | 0 | LTG
|  | Other - Baseboard Heater#3 | 1 | OTH
| 13 | Receptacle - 78,81 | 2 | REC | 1401 | 20A | 1P | R
|  | Lighting - 76 | 1 | LTG
|  | Other - Baseboard Heater#5 | 1 | OTH
| 14 | Receptacle - 86,83,79,75,76,70,89 | 7 | REC | 1780 | 20A | 1P | Y
|  | Lighting - 97,95,96,91,92,89,87,88,80,81,75,73,74,65,63 | 15 | LTG
|  | Other | 0 | OTH
| 15 | Receptacle | 0 | REC | 758 | 15A | 1P | B
|  | Lighting | 0 | LTG
|  | Other - Force Flow Fan#4 | 1 | OTH
| 16 | Receptacle | 0 | REC | 1800 | 40A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Dish Washer | 1 | OTH
| 17 | Receptacle | 0 | REC | 800 | 15A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - Fridge | 1 | OTH
| 18 | Receptacle - 2,3,4,6,7,8 | 6 | REC | 1119.1 | 20A | 1P | B
|  | Lighting - 1 | 1 | LTG
|  | Other | 0 | OTH
| 19 | Receptacle | 0 | REC | 1800 | 20A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Electrical Oven/Range | 1 | OTH
Receptacle 52 & 62 is 90VA | 20 | Receptacle - 64,65,60,52,62,51,40,49 | 8 | REC | 1336 | 20A | 1P | Y
|  | Lighting - 58,51,57,50,44 | 5 | LTG
|  | Other | 0 | OTH
Receptacle 17 is 90VA | 21 | Receptacle - 9,10,12,13,15,23,19,17 | 8 | REC | 1350 | 20A | 1P | B
|  | Lighting | 0 | LTG
|  | Other | 0 | OTH
| 22 | Receptacle | 0 | REC | 1000 | 20A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Fridge | 1 | OTH
Receptacle 50 is 360VA | 23 | Receptacle - 42,48,43,53,59,50,97 | 6 | REC | 1370 | 20A | 1P | Y
|  | Lighting - 49,52,42 | 3 | LTG
|  | Other - CCTV#15 | 1 | OTH
| 24 | Receptacle - 22,24,27,28 | 4 | REC | 1378 | 20A | 1P | B
|  | Lighting - 7,8,9,11,12,13 | 6 | LTG
|  | Other - Projector#1, CCTV#2 | 2 | OTH
| SPARE |  |  |  |  | 20A | 1P | R
| 25 | Receptacle - 69 | 1 | REC | 1210 | 15A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - Baseboard Heater#8 | 1 | OTH
| 26 | Receptacle - 32,33 | 2 | REC | 1211.2 | 15A | 1P | B
|  | Lighting - 15,16,17,20,21,22,23,24,26,28,30,27,29,31,32,33,34,35 | 18 | LTG
|  | Other - CCTV#4,6,8 Projector#2 | 2 | OTH
| 27 | Receptacle - 36,47 | 2 | REC | 1390 | 20A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Baseboard Heater#9 | 1 | OTH
| 28 | Receptacle | 0 | REC | 570 | 15A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - Hot Water Tank | 1 | OTH
Receptacle 39 is 360VA | 29 | Receptacle - 34,39,30,37,21 | 5 | REC | 1315 | 20A | 1P | B
|  | Lighting - 36,37,18,19 | 4 | LTG
|  | Other - CCTV#7,9 | 2 | OTH
| 30 | Receptacle | 0 | REC | 1579 | 30A | 1P | Y
|  | Lighting | 0 | LTG
|  | Other - Force Flow Fan#3 | 1 | OTH
| 31 | Receptacle | 0 | REC | 1290 | 15A | 1P | R
|  | Lighting | 0 | LTG
|  | Other - Projector#5,6,7 | 1 | OTH
| SPARE |  |  |  |  | 25A | 1P | Y
| SPARE |  |  |  |  | 15A | 1P | B

## Panel Board 2
DISTRIBUTION BOARD - 2P
Voltage : 208V |  |  |  | Bus Rating : 30A, 3PN
Phase : 3 |  |  |  | Main Breaker Rating : 30A, 3PN | [5 empty] | Connected Load (VA) | Spare (VA)
Wire : 4 |  |  |  | Location Name : Electrical Room 202 |  |  |  |  | Phase R-Y-B | 10520 | 960
Total Circuits : 5
Remarks | CCT No | Load |  |  |  | Breaker Size | Pole | Phase
|  | Description | Qty | Type | KVA
| 1 | Receptacle | 0 | REC | 2.63 | 10A | 2P | R-Y | Load Summary (VA) |  | Diversity | Demand Load
|  | Lighting | 0 | LTG |  |  |  |  | Receptacle | 0 | As per CEC for first 10KVA Diversity Factor is 1.0 & for rest 0.5 | 0
|  | Baseboard Heater#1 | 1 | HTR |  |  |  |  | Lighting | 0
| 2 | Receptacle | 0 | REC | 2.63 | 10A | 2P | Y-B | Baseboard Heater | 10520 | 0.5 | 5260
|  | Lighting | 0 | LTG |  |  |  |  | Spare | 960 | 0.5 | 480
|  | Baseboard Heater#4 | 1 | HTR
| 3 | Receptacle | 0 | REC | 2.63 | 10A | 2P | R-B
|  | Lighting | 0 | LTG |  |  |  |  | Total Demand (KVA) |  | 5.74
|  | Baseboard Heater#6 | 1 | HTR |  |  |  |  | Total Demand (Amps) |  | 13.7981
| 4 | Receptacle | 0 | REC | 2.63 | 10A | 2P | R-Y | Spare Load (Included in Total Demand) |  | 9.125%
|  | Lighting | 0 | LTG
|  | Baseboard Heater#7 | 1 | HTR |  |  |  |  | NOTES : A. For the sake of simplicity efficiency and power factor for Baseboard Heater are considered 95% and 0.95 respectively.
| 5 | SPARE |  |  |  | 10A | 1P | B

## Panel Board 3
DISTRIBUTION BOARD - 3P
Voltage : 208V |  |  |  | Bus Rating : 110A, 3PN
Phase : 3 |  |  |  | Main Breaker Rating : 110A, 3PN | [5 empty] | Connected Load (VA) | Spare (VA)
Wire : 4 |  |  |  | Location Name : Electrical Room 202 |  |  |  |  | Phase R-Y-B | 54430 | 5760
Total Circuits : 10
Remarks | CCT No | Load |  |  |  | Breaker Size | Pole | Phase
|  | Description | Qty | Type | KVA
| 1 | Receptacle | 0 | REC | 5.037 | 35A | 3P | R-Y-B | Load Summary (VA) |  | Diversity | Demand Load
|  | Lighting | 0 | LTG |  |  |  |  | Receptacle | 0 | As per CEC for first 10KVA Diversity Factor is 1.0 & for rest 0.5 | 0
|  | Condensate Unit#1 | 1 | CU |  |  |  |  | Lighting | 0
| 2 | Receptacle | 0 | REC | 6.477 | 45A | 3P | R-Y-B | Condensate | 38861 | 0.6 | 23316.6
|  | Lighting | 0 | LTG |  |  |  |  | Exhaust Fan | 1177 | 1 | 1177
|  | Condensate Unit#2 | 1 | CU |  |  |  |  | Furnace | 14392 | 0.6 | 8635.2
| 3 | Receptacle | 0 | REC | 14.033 | 100A | 3P | R-Y-B | Spare | 5760 | 0.5 | 2880
|  | Lighting | 0 | LTG
|  | Condensate Unit#3 | 1 | CU
| 4 | Receptacle | 0 | REC | 13.314 | 90A | 3P | R-Y-B | Total Demand (KVA) |  | 36.0088
|  | Lighting | 0 | LTG |  |  |  |  | Total Demand (Amps) |  | 86.5596
|  | Condensate Unit#4 | 1 | CU |  |  |  |  | Spare Load (Included in Total Demand) |  | 10.58%
| 5 | Receptacle | 0 | REC | 1.177 | 15A | 3P | R-Y-B
|  | Lighting | 0 | LTG |  |  |  |  | NOTES : A. For the sake of simplicity Diversity Factor for all the equipments is as shown in the above table.
|  | Exhaust Fan#2 | 1 | EF
| 6 | Receptacle | 0 | REC | 3.598 | 20A | 3P | R-Y-B
|  | Lighting | 0 | LTG
|  | Furnace#1 | 1 | FUR
| 7 | Receptacle | 0 | REC | 3.598 | 15A | 3P | R-Y-B
|  | Lighting | 0 | LTG
|  | Furnace#2 | 1 | FUR
| 8 | Receptacle | 0 | REC | 3.598 | 15A | 3P | R-Y-B
|  | Lighting | 0 | LTG
|  | Furnace#3 | 1 | FUR
| 9 | Receptacle | 0 | REC | 3.598 | 15A | 3P | R-Y-B
|  | Lighting | 0 | LTG
|  | Furnace#4 | 1 | FUR
| 10 | SPARE |  |  |  | 20A | 3P | R-Y-B

## Panel Board U
DISTRIBUTION BOARD - U
Voltage : 120/208V |  |  |  | Bus Rating : 70A, 3PN
Phase : 3 |  |  |  | Main Breaker Rating : 70A, 3PN | [5 empty] | Connected Load (VA) | Spare (VA)
Wire : 4 |  |  |  | Location Name : Electrical Room 202 |  |  |  |  | Phase R-Y-B | 16801 | 4320
Total Circuits : 7
Remarks | CCT No | Load |  |  |  | Breaker Size | Pole | Phase
|  | Description | Qty | Type | KVA
| 1 | Receptacle | 0 | REC | 15.705 | 150A | 3P | R-Y-B | Load Summary (VA) |  | Diversity | Demand Load
|  | Lighting | 0 | LTG |  |  |  |  | Receptacle | 0 | As per CEC for first 10KVA Diversity Factor is 1.0 & for rest 0.5 | 849.2
|  | Fire Pump | 1 | FP |  |  |  |  | Lighting | 849.2
| 2 | Receptacle | 0 | REC | 0.382 | 15A | 1P | R | Fire Pump | 15705 | 1 | 15705
|  | Lighting - 40,84,69,54,43,14,70,77 | 8 | LTG |  |  |  |  | Other | 246.5 | 1 | 246.5
|  | Other - CCTV#11,13,20 | 3 | CU |  |  |  |  | Spare | 4320 | 0.75 | 3240
| 3 | Receptacle | 0 | REC | 0.359 | 15A | 1P | Y
|  | Lighting - 94,64,79,93,41,25,10,4,5 | 9 | LTG
|  | Other - CCTV#18,21,12,5,3,19 | 6 | CU |  |  |  |  | Total Demand (KVA) |  | 20.0407
| 4 | Receptacle | 0 | REC | 0.355 | 15A | 1P | B | Total Demand (Amps) |  | 55.6291
|  | Lighting - 2,3,6 | 0 | LTG |  |  |  |  | Spare Load (Included in Total Demand) |  | 25.71%
|  | Other - Exhaust Fan#1, CCTV#26 | 2 | CU
| 5 | SPARE |  |  |  | 15A | 1P | R | NOTES : A. For the sake of simplicity Diversity Factor for all the equipments is as shown in the above table.
| 6 | SPARE |  |  |  | 15A | 1P | Y
| 7 | SPARE |  |  |  | 15A | 1P | B