## Mechanical Schedule
|  |  | Nameplate |  |  |  | OC Protection |  |  | Feeder |  |  |  | Disconnect |  |  |  | Starter/VFD |  |  |  |  | Starter Control
Unit no. | Description | Location | Voltage | Phase | MCA | Load | Type | Rating | Poles | Conductor | Bond | Conduit | Fed From | NEMA Rating | S | I | C | Type | NEMA Rating | S | I | C | Type | Remote Type | N/O Contacts | N/C Contacts | S | I | C | Remarks
CU-1 | Condensing Unit | Exterier- South Cultural Activity | 208 | 3 | 17.5 | 14 FLA | MCB | 35A | 3P | AWG #8 |  | 27mm | 3P-CKT-1 | 4X | NA |  |  | Manual Starter | NA |  |  |  | INT | NA | NA |  |  |  |  | Controlled by Furnace
CU-2 | Condensing Unit | Exterier- South Cultural Activity | 208 | 3 | 22.5 | 18 FLA | MCB | 45A | 3P | AWG #6 |  | 35mm | 3P-CKT-2 | 4X | NA |  |  | Manual Starter | NA |  |  |  | INT | NA | NA |  |  |  |  | Controlled by Furnace
CU-3 | Condensing Unit | Exterier- South Cultural Activity | 208 | 3 | 50 | 39 FLA | MCB | 100A | 3P | 1/0 |  | 53mm | 3P-CKT-3 | 4X | NA |  |  | Manual Starter | NA |  |  |  | INT | NA | NA |  |  |  |  | Controlled by Furnace
CU-4 | Condensing Unit | Exterier- South Cultural Activity | 208 | 3 | 47.5 | 37 FLA | MCB | 90A | 3P | 1/0 |  | 53mm | 3P-CKT-4 | 4X | NA |  |  | Manual Starter | NA |  |  |  | INT | NA | NA |  |  |  |  | Controlled by Furnace
F-1 | Furnace | Mechanical Room 117 | 208 | 3 |  | 10 FLA | MCB | 20A | 3P | AWG #10 |  | 21mm | 3P-CKT-6 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
F-2 | Furnace | Mechanical Room 117 | 208 | 3 |  | 10 FLA | MCB | 15A | 3P | AWG #12 |  | 21mm | 3P-CKT-7 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
F-3 | Furnace | Mechanical Room 203 | 208 | 3 |  | 10 FLA | MCB | 15A | 3P | AWG #12 |  | 21mm | 3P-CKT-8 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
F-4 | Furnace | Mechanical Room 203 | 208 | 3 |  | 12 FLA | MCB | 15A | 3P | AWG #12 |  | 21mm | 3P-CKT-9 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
DHWT-1 | Domestic Hot Water Tank | Mechanical Room 203 | 120 | 1 |  | 5 FLA | MCB | 15A | 1P | AWG #12 |  | 21mm | 1P-CKT-28 | NA | NA |  |  | NA | NA |  |  |  | INT | NA | NA
EF-1 | Exhaust Fan | Mechanical Room 203 | 120 | 1 | 7.5 | 0.25 HP | MCB | 15A | 1P | AWG #12 |  | 21mm | U-CKT-4 | 4X | NA |  |  | Manual Starter | NA |  |  |  | COMB | NA | NA |  |  |  |  | Interlocker local lighting
EF-2 | Exhaust Fan | Vestibule 120 | 208 | 3 | 8.75 | 1.5 HP | MCB | 15A | 3P | AWG #12 |  | 21mm | 3P-CKT-5 | 4X | NA |  |  | Manual Starter | NA |  |  |  | VFD | NA | NA |  |  |  |  | Interlocker local lighting
BB-1 | Baseboard Heater | Kitchen 108 | 208 | 1 |  | 2.5 kW | MCB | 10A | 2P | AWG #12 |  | 21mm | 2P-CKT-1 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
BB-2 | Baseboard Heater | Kitchen 108 | 120 | 1 |  | 1 kW | MCB | 15A | 1P | AWG #12 |  | 21mm | 1P-CKT-2 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
BB-3 | Baseboard Heater | Common 109 | 120 | 1 |  | 1 kW | MCB | 20A | 1P | AWG #12 |  | 21mm | 1P-CKT-12 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
BB-4 | Baseboard Heater | Common 109 | 208 | 1 |  | 2.5 kW | MCB | 10A | 2P | AWG #12 |  | 21mm | 2P-CKT-2 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
BB-5 | Baseboard Heater | Common 109 | 120 | 1 |  | 1 kW | MCB | 20A | 1P | AWG #12 |  | 21mm | 1P-CKT-13 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
BB-6 | Baseboard Heater | Cultural Activity Room 110 | 208 | 1 |  | 2.5 kW | MCB | 10A | 2P | AWG #12 |  | 21mm | 2P-CKT-3 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
BB-7 | Baseboard Heater | Cultural Activity Room 110 | 208 | 1 |  | 2.5 kW | MCB | 10A | 2P | AWG #12 |  | 21mm | 2P-CKT-4 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
BB-8 | Baseboard Heater | Mens Washroom 104 | 120 | 1 |  | 1 kW | MCB | 15A | 1P | AWG #12 |  | 21mm | 1P-CKT-25 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
BB-9 | Baseboard Heater | Common 109 | 120 | 1 |  | 1 kW | MCB | 20A | 1P | AWG #12 |  | 21mm | 1P-CKT-27 | NA | NA |  |  | NA | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
FF-1 | Force Flow Fan | Foyer 100 | 120 | 1 | 7.5 | 6 FLA | MCB | 15A | 1P | AWG #12 |  | 21mm | 1P-CKT-9 | 4X | NA |  |  | Manual Starter | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
FF-2 | Force Flow Fan | Vestibule 120 | 120 | 1 | 30 | 1.5 kW | MCB | 60A | 1P | AWG #4 |  | 27mm | 1P-CKT-3 | 4X | NA |  |  | Manual Starter | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
FF-3 | Force Flow Fan | Mechanical Room 117 | 120 | 1 | 16.25 | 1.5 kW | MCB | 30A | 1P | AWG #10 |  | 21mm | 1P-CKT-30 | 4X | NA |  |  | Manual Starter | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
FF-4 | Force Flow Fan | Water Meter 107 | 120 | 1 | 7.5 | 6 FLA | MCB | 15A | 1P | AWG #12 |  | 21mm | 1P-CKT-15 | 4X | NA |  |  | Manual Starter | NA |  |  |  | LTST | NA | NA |  |  |  |  | Controlled by Thermostate
FP | Fire Pump | Mechanical Room 203 | 208 | 3 | 75 | 20 HP | MCB | 150A | 3P | 4/0 |  | 63mm | U-CKT-1 | 4X | NA |  |  | Manual Starter | NA |  |  |  |  | NA | NA |  |  |  |  | Controlled by Thermostate